## Elec+Mech
DC Side Components
Description | Specification | Unit | value determination logic | brief logic | Quantity | Unit Rate | Total Amount | fetch from detailed summary
Solar PV Modules | Mono PERC/TOPCon, W, Efficiency ≥ % | Nos | fetch from detailed summary | get it from design summary tab |  |  |  | calculated & estimated
MC4 Connectors | Male & Female pairs | Pairs | calculated & estimated | refer to total string numbers and strings input per inverter |  |  |  | constant value/lumpsum per project
Module Mounting Structure (MMS)
MMS Foundation | RCC/Ramming/Screw pile | Nos/MT | calculated & estimated | refer to pv mounting structural type, total qty of such pv mounting structure
Vertical Posts | HDG Steel, C-channel/I-section | MT | calculated & estimated | refer to pv mounting structural type, total qty of such pv mounting structure
Purlins/Rails | HDG Steel, C-channel | MT | calculated & estimated | refer to pv mounting structural type, total qty of such pv mounting structure
Columns |  |  | calculated & estimated | refer to pv mounting structural type, total qty of such pv mounting structure
Struture Earthing Material |  |  | calculated & estimated
DC Cables & Accessories
DC Cable (String level) | 4/6 mm² Solar cable, 1.5kV | km | fetch from detailed summary | get it from design summary tab
DC Cable (Combiner to Inverter) | 95/120/150/185 mm² XLPE, 1.5kV | km | fetch from detailed summary | get it from design summary tab
String Combiner Boxes (SCB/DCDB)
DCDB Enclosure | IP65, Thermoplastic/MS | Nos | fetch from detailed summary | get it from design summary tab
DC Fuses | 15A, 1000V DC, gPV | Nos | fetch from detailed summary | get it from design summary tab
Fuse Holders | 1000V DC rated | Nos | fetch from detailed summary | get it from design summary tab
DC SPD | Type 2, 1000V DC | Nos | fetch from detailed summary | get it from design summary tab
DC MCB/Isolator | 1000V DC rated | Nos | fetch from detailed summary | get it from design summary tab
DC Bus Bars & Terminals for DCDB | Copper, Tinned | Set | fetch from detailed summary | get it from design summary tab
Cable Ties & Clips | UV resistant | Nos | calculated & estimated | as per industry's tandard estimation and application methodology
Cable Trays | Perforated GI | m | calculated & estimated | refer to DCDB to inverter dc cable length
POWER CONVERSION SYSTEM
Central/String Inverters | MW, 1500V DC input | Nos | fetch from detailed summary | get it from design summary tab
Inverter Container/Housing | With HVAC, 40ft | Nos | calculated & estimated | based on inverter type and the dimension, one container should be around 10m long and 4m height approx, rest estimation should be as per industry standard
Inverter Protection System | DC/AC protection panels | Set | calculated & estimated | as per industry's tandard estimation and application methodology
LV Combiner panel (for String Inverters) |  |  | fetch from detailed summary | get it from design summary tab
Low Voltage Switchgear
Circuit Breaker#1 (Inv to LV Combiner Panel) | MCCB/ACB | Nos | fetch from detailed summary | get it from design summary tab
Circuit Breaker#2 (LV Combiner Panel IDT) | MCCB/ACB |  | fetch from detailed summary | get it from design summary tab
MV Transformer Station
Inverter Duty Transformer | 0.69/ kV, MVA, ONAN/ONAF | Nos | fetch from detailed summary | get it from design summary tab
Transformer Foundation | RCC with oil pit | Nos | calculated & estimated | based on transformer nos from design summary tab and based on industry standard and common practice of foundation allocation and design based on its MVA rating and types
HV Bushings & Arrestors | kV rated | Set | calculated & estimated | based on transformer nos from design summary tab and based on industry standard and common practice of Hv bushing and arrestors capacity estimation and qty allocation
Neutral Grounding Resistor | Brief Specification required | Nos | calculated & estimated | based on transformer nos from design summary tab and based on industry standard and common practice of Neutral Grounding Resistor estimation and qty allocation
Oil Testing Kit | Portable | Nos | calculated & estimated | based on transformer nos from design summary tab and based on industry standard and common practice of estimation and qty allocation
Medium Voltage Switchgear
Ring Main Unit (RMU) | kV, SF6/Vacuum | Nos
MV Switchgear Panel | Metal clad, kV | Nos | calculated & estimated | refer to the HT design configuration section in design summary tab, and follow the industry stanadrd practice to design and estimate the MV SwitchGear panel
Circuit Breaker | VCB/SF6, A, kV | Nos | fetch from detailed summary | get it from design summary tab
Protection Relays | Numerical, multifunctional | Nos | calculated & estimated | refer to the HT design configuration section in design summary tab, and follow the industry stanadrd practice to design and estimate the protection relays for MV circuit
CT & PT for Metering | kV, accuracy class 0.2 | Sets | calculated & estimated | refer to the HT design configuration section in design summary tab, and follow the industry stanadrd practice to calculate and estimate the CT PT ratings for solar metering
LV AC Cables
LV Power Cable#1 (Central Inv to IDT) | 3.5C x mm² XLPE/XLPO | km | fetch from detailed summary | get it from design summary tab
LV Power Cable#2(String Inv to LV Combiner Panel) | 3.5C x mm² XLPE/XLPO | km | fetch from detailed summary | get it from design summary tab
LV Power Cable#3(LV Combiner Panel to IDT) | 3.5C x mm² XLPE/XLPO | km | fetch from detailed summary | get it from design summary tab
Cable Termination Kits | Heat shrink/Cold shrink | Sets | calculated & estimated | refer to design sumarry tab for cables from various circuits in the ac side design of the pv system and follows the indsutry's standard and common practice
Cable Jointing Kits | Straight through | Sets | calculated & estimated | refer to design sumarry tab for cables from various circuits in the ac side design of the pv system and follows the indsutry's standard and common practice
MV AC Cables
MV Power Cable | 3C x mm² XLPE, kV | km | fetch from detailed summary | get it from design summary tab
Cable Termination Kits | Outdoor/Indoor type | Sets | calculated & estimated | refer to design sumarry tab for cables from various circuits in the ac side design of the pv system and follows the indsutry's standard and common practice
Cable Jointing Kits | Straight/Transition | Sets | calculated & estimated | refer to design sumarry tab for cables from various circuits in the ac side design of the pv system and follows the indsutry's standard and common practice
Cable Fault Locator | Portable | Nos | constant value/lumpsum per project | refer to design sumarry tab for cables from various circuits in the ac side design of the pv system and follows the indsutry's standard and common practice
Cable Laying & Management
Cable Trenching | 1.2m depth | km | calculated & estimated | this includes the DC cable trench and AC cable trench both, for ground mount installation, we can consider both the AC and DC cables passing through the trench, you need to apply industry standard method to estimate the cable trench length and depths based on the project parameters
Cable Trays (Plant room) | HDG, ladder type | m | calculated & estimated | based on the inverters' dc input side entry points lengths - vertical and small portion f horizontal length for dc side cables and control rooom, inevrter output vertical runs and transformers' input and output sides' small vertical runs can use trays and the communication cables also shall be using the cable trays for vertical runs mainly, estimate the overall length based on teh system design parameters and design summary and based on industry standard
Warning Tape | "Danger" printed | km | constant value/lumpsum per project | as per industry's standard estimation and application methodology
Route Markers | RCC/FRP | Nos | calculated & estimated | as per industry's standard estimation and application methodology
Main Substation Equipment
Power Transformer | / kV, MVA | Nos | fetch from detailed summary | get it from design summary tab
HV Circuit Breaker | kV, SF6/Vacuum | Nos | fetch from detailed summary | get it from design summary tab
Isolators | kV, motorized | Sets | calculated & estimated | refer to the HT design configuration section in design summary tab, and follow the industry stanadrd practice to design and estimate the motorized isolators for HV circuit/ at the plant sub-station level
Current Transformer | kV, metering + protection | Nos | calculated & estimated | refer to the HT design configuration section in design summary tab, and follow the industry stanadrd practice to calculate and estimate the CT PT ratings for solar metering
Potential Transformer | kV, metering + protection | Nos | calculated & estimated | refer to the HT design configuration section in design summary tab, and follow the industry stanadrd practice to calculate and estimate the CT PT ratings for solar metering
Lightning Arrestor | kV, gapless | Nos | calculated & estimated | based on overall pv area's dimension and common industry practice and standard
Control & Relay Panel
Control & Relay Panel | Simplex/Duplex | Nos | calculated & estimated | as per industry's standard estimation and application methodology
Distance Protection Relay | Numerical | Nos | calculated & estimated | as per industry's standard estimation and application methodology
Differential Protection | Transformer/Line | Nos | calculated & estimated | as per industry's standard estimation and application methodology
SCADA RTU | IEC 61850 compatible | Nos | calculated & estimated | as per industry's standard estimation and application methodology
GPS Time Synchronization | Master clock | Set | calculated & estimated | as per industry's standard estimation and application methodology
Substation Auxiliary
Station Transformer | kVA, /0.433kV | Nos | calculated & estimated | as per industry's standard estimation and application methodology
LT Distribution Panel | With AMF | Nos | calculated & estimated | as per industry's standard estimation and application methodology
DG Set | kVA, with AMF | Nos | calculated & estimated | as per industry's standard estimation and application methodology
Battery Bank | 110/220V DC, AH | Set | calculated & estimated | as per industry's standard estimation and application methodology
Battery Charger | Float cum boost | Nos | calculated & estimated | as per industry's standard estimation and application methodology
DC Distribution Board | With monitoring | Nos | calculated & estimated | as per industry's standard estimation and application methodology
Transmission Line
Transmission Towers | kV, lattice type | Nos | fetch from detailed summary | based on the user's input details of distance between Nearest Grid point to Plant sub-station end, calculate the transmission line distance, type of cable to be used as per industry standard and based on voltage level and current carrying capacity, and calculate the towers numbers based on cable's sag and tension calculation and estimation
Conductors | ACSR/AAAC sq.mm | km | calculated & estimated
Ground Wire | OPGW/Earth wire | km | calculated & estimated
Insulators | Disc/Polymer type | Nos | calculated & estimated
Tower Foundation | RCC | Nos | calculated & estimated
Plant Earthing System
Equipment Earthing | 50x6mm GI Strip | km | calculated & estimated | as per industry's standard estimation and application methodology, and based on inverter, transfomrers short circuit current ratings (calculate), inverter and control room estimatation and sub-station area and eshort-circuit current estimation for earthing grid calculation, and follow the IEC standard for earthing material, crosss ection, eletrodes proeprty, pit chambers etc spefication and quantities
Earthing Grid | 40x6mm GI Strip | km | calculated & estimated
Earth Electrodes | CI pipe, 100mm dia, 3m | Nos | calculated & estimated
Earth Enhancement Material | Bentonite/GEM | MT | calculated & estimated
Earth Pit Chambers | With cover plate | Nos | calculated & estimated
Exothermic Welding | Molds and powder | Sets | calculated & estimated
Lightning Protection System
Lightning Masts | 15-20m height | Nos | calculated & estimated | as per industry's standard estimation and application methodology and based on the project capacity and equipment and circuit details which can be fetched from design summary tab
Air Terminals | Franklin rod type | Nos | calculated & estimated
Down Conductors | 70mm² Aluminum | km | calculated & estimated
Equipotential Bonding | At inverter/transformer | LS | calculated & estimated
SCADA System
SCADA Server | Redundant, industrial PC | Set | calculated & estimated | as per industry's standard estimation and application methodology based on the project capacity and equipment and circuit details which can be fetched from design summary tab
SCADA Software | Licensed, unlimited tags | Nos | constant value/lumpsum per project
Operator Workstation | With dual monitors | Nos | calculated & estimated
Network Equipment | Managed switches, routers | Set | constant value/lumpsum per project
Firewall | Industrial grade | Nos | constant value/lumpsum per project
UPS for SCADA | 10kVA, 30 min backup | Nos | calculated & estimated
Weather Monitoring Station
Pyranometer | Class A, with tracker | Nos | calculated & estimated | as per industry's standard estimation and application methodology and strictly following IEC 61724 (latest edition) and based on the project capacity and equipment and circuit details which can be fetched from design summary tab
Module Temperature Sensor | PT100 | Nos | calculated & estimated
Ambient Temperature | With radiation shield | Nos | calculated & estimated
Wind Speed & Direction | Ultrasonic type | Nos | calculated & estimated
Rain Gauge | Tipping bucket | Nos | calculated & estimated
Data Logger | With remote transmission | Nos | calculated & estimated
Reference Cell | Calibrated | Nos | calculated & estimated
Soiling Station | With measurement | Nos | calculated & estimated
Communication System
Optical Fiber Cable | 24 core, armored | km | calculated & estimated | as per industry's standard estimation and application methodology based on the project capacity and equipment and circuit details which can be fetched from design summary tab
OFC Accessories | Joint boxes, pigtails | Set | calculated & estimated
RTU/Data Concentrators | At field level | Nos | calculated & estimated
Firefighting Equipment
Fire Extinguishers | CO2/ABC Powder, 6kg | Nos | calculated & estimated | as per industry's standard estimation and application methodology based on the project capacity and equipment and circuit details which can be fetched from design summary tab
Fire Hydrant System | Complete with pumps | Set | calculated & estimated
Water Sprinkler System | For buildings | m² | calculated & estimated
Fire Detection System | Smoke/heat detectors | Set | calculated & estimated
Fire Alarm Panel | Addressable type | Nos | calculated & estimated
Emergency Lighting | LED, battery backup | Nos | calculated & estimated
Power Quality Equipment
Power Quality Analyzer | Class A, IEC 61000-4-30 | Nos | calculated & estimated | as per industry's standard estimation and application methodology based on the project capacity and equipment and circuit details which can be fetched from design summary tab
Reactive Power Compensation | STATCOM/SVC | Set | calculated & estimated
Power Factor Correction | Capacitor banks | kVAR | calculated & estimated
Grid Compliance Equipment
Anti-Islanding Relay | IEEE 1547 compliant | Nos | calculated & estimated | as per industry's standard estimation and application methodology based on the project capacity and equipment and circuit details which can be fetched from design summary tab
Frequency Relay | Over/Under frequency | Nos | calculated & estimated
Voltage Relay | Over/Under voltage | Nos | calculated & estimated
Synchroscope | For synchronization | Nos | calculated & estimated
Testing Equipment
Earth Tester | Digital, 4-pole method | Nos | calculated & estimated | as per industry's standard estimation and application methodology based on the project capacity and equipment and circuit details which can be fetched from design summary tab
Insulation Tester | 5kV, digital | Nos | calculated & estimated
Multimeter | True RMS, CAT IV | Nos | calculated & estimated
Oscilloscope | 4-channel, 100MHz | Nos | calculated & estimated
Power Analyzer | 3-phase, harmonics | Nos | calculated & estimated
High Pot Tester | AC/DC, 100kV | Nos | calculated & estimated
O&M Equipment
Module Cleaning Equipment | Water fed/Robotic | Set | calculated & estimated | as per industry's standard estimation and application methodology based on the project capacity and equipment and circuit details which can be fetched from design summary tab
Thermal Imaging Camera | For inspection | Nos | constant value/lumpsum per project
I-V Curve Tracer | For module testing | Nos | constant value/lumpsum per project
Irradiance Meter | Portable | Nos | constant value/lumpsum per project
Spare Parts (2 Years)
String Fuses | 20/25A, 1500V DC | Nos | calculated & estimated | as per industry's standard estimation and application methodology based on the project capacity and equipment and circuit details which can be fetched from design summary tab
DC Contactors | For combiner boxes | Nos | calculated & estimated
Protection Relays | 5% of total | Nos | calculated & estimated
HV Fuses | For transformers | Nos | calculated & estimated
Cable Joints | Emergency stock | Sets | calculated & estimated
Inverter Cooling Fans | Replacement | Nos | calculated & estimated