| Input Parameters | From where the values to be taken/ default values for some parameters |
| --- | --- |
| 1. DC Side Inputs |  |
| Structure type | From PV areas tab |
| Module width (mm) | From PV select tab |
| Module length (mm) | From PV select tab |
| Total number of tables | From PV areas tab |
| Module layout per table (for example: “2P×5” or “3L×8”) | From PV Areas tab, table configuration section |
| Total number of rows (only required if structure type = Ballasted) | From PV Areas tab |
| String short-circuit current (A) | equals single PV Mdoule Short-circuit Current; From PV select tab |
| Total number of strings per inverter | From DC Config tab (Inverter parameter detail section |
| 2. Lightning Protection Inputs |  |
| Total plant area (in square meters) | From PV areas tab |
| Soil type at the site (choose one: saturated clay, clay, loam, moist sand, dry sand, rock) | From Location Tab (Soil type selection section) |
| 3. AC Side – Common Inputs |  |
| System type (choose one: LV Connection type, HV connection type) | From AC Config tab |
| Number of inverters | From DC Config tab |
| 4. AC Side – LV Connection type |  |
| Inverter output voltage (V) | From dc config tab, under the Inverter section |
| Inverter output current (A, per inverter) | From dc config tab, under the Inverter section |
| Distance from each inverter to the AC combiner panel (m) | From ac config tab, under the cable sizing section |
| AC phase cable cross-section from inverter to AC combiner (mm²) | From ac config tab, under the cable sizing section |
| Distance from AC combiner panel to the Point of Connection (m) | From ac config tab, under the cable sizing section |
| AC phase cable cross-section from combiner to PoC (mm²) | From ac config tab, under the cable sizing section |
| Current rating of AC combiner panel incomer breaker (A) | From ac config tab, under the circuit breaker sizing section |
| Current rating of AC combiner panel outgoing breaker (A) | From ac config tab, under the circuit breaker sizing section |
| 5. AC Side – HV connection type + String Inverter Inputs |  |
| Number of String inverters | from dc config tab |
| Inverter output voltage (V) | From dc config tab, under the Inverter section |
| Inverter output current (A, per inverter) | From dc config tab, under the Inverter section |
| No of Inverters connected to LV AC Combiner Panel | From ac config tab, under the cable sizing section |
| Total no of LV AC Combiner Panel | From ac config tab, under the cable sizing section |
| Distance from LV AC combiner panel to the Point of Connection (m) | From ac config tab, under the cable sizing section |
| AC phase cable cross-section from combiner to PoC (mm²) | From ac config tab, under the cable sizing section |
| Inverter Duty Transformers (IDT): |  |
| Quantity of IDTs | from ac config tab, under the IDT config section |
| Input voltage (V) of each IDT | from ac config tab, under the IDT config section |
| Input current (A) of each IDT | from ac config tab, under the IDT config section |
| Output voltage (V) of each IDT | from ac config tab, under the IDT config section |
| Output current (A) of each IDT | from ac config tab, under the IDT config section |
| Power Transformers (PT): |  |
| Quantity of PTs |  |
| Input voltage (V) of each PT | from ac config tab, under the PT config section |
| Input current (A) of each PT | from ac config tab, under the PT config section |
| Output voltage (V) of each PT | from ac config tab, under the PT config section |
| Output current (A) of each PT | from ac config tab, under the PT config section |
| Cable details: |  |
| Distance from each inverter to the AC combiner panel (m) | From ac config tab, under the cable sizing section |
| AC phase cable cross-section from inverter to AC combiner (mm²) | From ac config tab, under the cable sizing section |
| Distance from LV Combiner Panel to IDT (m) | From ac config tab, under the ac cable sizing section |
| Phase cable size from LV Combiner Panel to IDT (mm²) | From ac config tab, under the ac cable sizing section |
| Distance from IDT to PT (m) | From ac config tab, under the ac cable sizing section |
| Phase cable size from IDT to PT (mm²) | From ac config tab, under the ac cable sizing section |
| Distance from PT to PoC (m) | From ac config tab, under the ac cable sizing section |
| Phase cable size from PT to PoC (mm²) | From ac config tab, under the ac cable sizing section |
| Transformer details: |  |
| Transformer MVA rating | From Ac config tab, under the IDT and PT config section |
| Transformer percentage impedance (%Z) | Consider 6% as default for IDT and PT |
| Circuit Breaker details: |  |
| Current rating of AC combiner panel incomer breaker (A) | From ac config tab, under the circuit breaker sizing section |
| Current rating of AC combiner panel outgoing breaker (A) | From ac config tab, under the circuit breaker sizing section |
| Circuit Breaker Type from Central Inverter to IDT | From ac config tab, under the circuit breaker sizing section |
| Circuit Breaker Rating from Central Inverter to IDT | From ac config tab, under the circuit breaker sizing section |
| Circuit Breaker Type from IDT to PT | From ac config tab, under the circuit breaker sizing section |
| Circuit Breaker Rating from IDT to PT | From ac config tab, under the circuit breaker sizing section |
| Circuit Breaker Type from PT to PoC | From ac config tab, under the circuit breaker sizing section |
| Circuit Breaker Rating from PT to PoC | From ac config tab, under the circuit breaker sizing section |
| 6. AC Side – HV connection type + Central Inverter Inputs |  |
| Number of central inverters | from dc config tab |
| Inverter Duty Transformers (IDT): |  |
| Quantity of IDTs | from ac config tab, under the IDT config section |
| Input voltage (V) of each IDT | from ac config tab, under the IDT config section |
| Input current (A) of each IDT | from ac config tab, under the IDT config section |
| Output voltage (V) of each IDT | from ac config tab, under the IDT config section |
| Output current (A) of each IDT | from ac config tab, under the IDT config section |
| Power Transformers (PT): |  |
| Quantity of PTs |  |
| Input voltage (V) of each PT | from ac config tab, under the PT config section |
| Input current (A) of each PT | from ac config tab, under the PT config section |
| Output voltage (V) of each PT | from ac config tab, under the PT config section |
| Output current (A) of each PT | from ac config tab, under the PT config section |
| Cable details: |  |
| Distance from inverter to IDT (m) | From ac config tab, under the ac cable sizing section |
| Phase cable size from inverter to IDT (mm²) | From ac config tab, under the ac cable sizing section |
| Distance from IDT to PT (m) | From ac config tab, under the ac cable sizing section |
| Phase cable size from IDT to PT (mm²) | From ac config tab, under the ac cable sizing section |
| Distance from PT to PoC (m) | From ac config tab, under the ac cable sizing section |
| Phase cable size from PT to PoC (mm²) | From ac config tab, under the ac cable sizing section |
| Transformer details (optional, if available): |  |
| Transformer MVA rating | From Ac config tab, under the IDT and PT config section |
| Transformer percentage impedance (%Z) | Consider 6% as default for IDT and PT |
| Circuit Breaker Type from Central Inverter to IDT | From ac config tab, under the circuit breaker sizing section |
| Circuit Breaker Rating from Central Inverter to IDT | From ac config tab, under the circuit breaker sizing section |
| Circuit Breaker Type from IDT to PT | From ac config tab, under the circuit breaker sizing section |
| Circuit Breaker Rating from IDT to PT | From ac config tab, under the circuit breaker sizing section |
| Circuit Breaker Type from PT to PoC | From ac config tab, under the circuit breaker sizing section |
| Circuit Breaker Rating from PT to PoC | From ac config tab, under the circuit breaker sizing section |
| 7. Substation Inputs |  |
| Substation yard size | consider default value as 30×30 m for LV systems, 40×40 m for HV systems |
| Target earthing resistance (Ω) | consider default is 5 Ω for LV systems, 1 Ω for HV systems |
| 8. Fixed Preferences (always the same, no input required from user) |  |
| Protective device | consider default as String fuse |
| Preferred material = Tinned copper | consider default as tinned copper |
| Preferred insulation = PVC | consider default as PVC |
| Rail bonding mode = Bonding clamps | consider default as bonding clips |
| Drop rule | one drop per N tables (where N depends on structure type and is defined in rules, not user input) |
| 9. Transformer Earthing Inputs |  |
| Number of IDTs (already listed in HV inputs) | from ac config tab |
| Number of PTs (already listed in HV inputs) | consider always 1 for HV connection type systems |
| Transformer earthing | Consider 2 dedicated earth pits for neutral earthing + 2 dedicated earth pits for body earthing |